## Sheet1
| Measured parameter: | Explanation of marks: | Comments
1 | Date/Time | It is date and time of measurement evry 10 min. | Devices OTLM are fixed on conductors on left and right side of tower (see enclosed photos).
2 | Line Temperature [Â°C] DEV1 | This is temperature measured on conductor with device 1* | Device is OTLM (overhead temperature line measurement) located bettwen tower No.12-13
3 | Line Temperature [Â°C] DEV2 | This is temperature measured on conductor with device 2* | Device 2 is OTLM (overhead temperature line measurement) located bettwen tower No.13-14
4 | Ambient Temperature OTLM [Â°C] DEV1 | Device 1 also measures average temperature of ambient between towers No.12-13 | Inside device we have two termoeters: one is on conductor and second is outside measuring air temperature. Also device has inclinometer in order to measure angle of conductor
5 | Ambient Temperature OTLM [Â°C] DEV2 | Device 2 also measures average temperature of ambient between towers No.13-14
6 | Line Current [A] DEV1 | Device 1 also measured current in conductor between towers No.12-13 | Generally it should be the same for both side of conductors, but scatter due by noise can occurred.
7 | Line Current [A] DEV2 | Device 2 also measures current in conductor between towers No.13-14
8 | Humidity [%] DEV1 | Device 1 measures Humidity of air between towers No.12-13
9 | Humidity [%] DEV2 | Device 2 measures humidity of air between towers No.13-14
10 | Angle [Â°] DEV1 | Device 1 measures angle of conductor at place where is fixed on conductor between towers No.12-13
11 | Angle [Â°] DEV2 | Device 2 measures angle of conductor at place where is fixed on conductor between towers No.13-14
12 | longitude | This is GPS position of tower
13 | latitude | This is GPS position of tower
14 | altitude [m] | This is GPS position of tower
15 | Vbat [V] | This is status of battery on tower, which is charged by solar energy
16 | ACC1 RMS [mm/s] | ACC1 RMS (mm / s) "Root Mean Square (RMS)" is the measured effective energy in a signal response and is determined as the sum of the squares of all deviations of the waveform f (t) from the equilibrium position with respect to the period of oscillation at the 1st accelerometer | This is measurements of vibration by accelormeter in direction of conductor line
17 | ACC1 PA1 [mm/s] | ACC1 PA1 (mm / s) is the vibration intensity at the first most expressed frequency at the 1st accelerometer
18 | ACC1 PF1 [Hz] | ACC1 PF1 (Hz) is the value of the first most expressed frequency at the 1st accelerometer
19 | ACC1 PA2 [mm/s] | ACC1 PA2 (mm / s) is the vibration intensity at the second most pronounced frequency at the 1st accelerometer
20 | ACC1 PF2 [Hz] | ACC1 PF2 (Hz) is the value of the second most pronounced frequency at the 1st accelerometer
21 | ACC1 PA3 [mm/s] | ACC1 PA3 (mm / s) is the vibration intensity at the third most pronounced frequency at the 1st accelerometer
22 | ACC1 PF3 [Hz] | ACC1 PF3 (Hz) is the value of the third most pronounced frequency at the 1st accelerometer
23 | ACC1 Fcross [Hz] | ACC1 Farcross (Hz) is the number of oscillations through the mean RMS value.
24 | ACC2 RMS [mm/s] | ACC2 RMS (mm / s) Root Mean Square (RMS) is the measured effective energy in a signal response and is determined as the sum of squares of all deviations of waveform f (t) from equilibrium position with respect to the period of oscillation at the 2nd accelerometer. | Analogous to the second accelerometer measuring perpendicular to the 1st accelerometer
25 | ACC2 PA1 [mm/s] | ACC2 PA1 (mm / s) is the vibration intensity at the first most expressed frequency at the 2nd accelerometer
26 | ACC2 PF1 [Hz] | ACC2 PF1 (Hz) is the value of the first most expressed frequency at the 2nd accelerometer
27 | ACC2 PA2 [mm/s] | ACC2 PA2 (mm / s) is the vibration intensity at the second most pronounced frequency at the 2nd accelerometer
28 | ACC2 PF2 [Hz] | ACC2 PF2 (Hz) is the value of the second most pronounced frequency at the 2nd accelerometer
29 | ACC2 PA3 [mm/s] | ACC2 PA3 (mm / s) is the vibration intensity at the third most pronounced frequency at 2. Accelerometer
30 | ACC2 PF3 [Hz] | ACC2 PF3 (Hz) is the value of the third most pronounced frequency at the 1st accelerometer
31 | ACC2 Fcross [Hz] | ACC2 Farcross (Hz) is the number of oscillations through the mean RMS value.
32 | Stress1 Ch1 Avg [MPa] | Mesurements of average stresses in Strain Gauge 1 (SG on chanel 1) in last 30 seconds before recording | Each tower has 4 legs with "L" profile. On each "L" profile we have Strain Gauge on both side of "L" profile. This two side are marked as Chanel 1 and Chanel 2.
33 | Stress1 Ch1 MaxAvg [MPa] | Mesurements of Maximum stresses in Strain Gauge 1 (SG on chanel 1) in last 30 seconds before recording | It is leg No. 1!
34 | Stress1 Ch1 MinAvg [MPa] | Mesurements of minimum stresses in Strain Gauge 1 (SG on chanel 1) in last 30 seconds before recording
35 | Stress1 Ch1 StdDev [MPa] | Standard deviation of measured stresses by SG 1 (on chanel 1) in last 30 seconds before recoding
36 | Stress1 Ch1 Fcross [Hz] | It is allways zero
37 | Stress1 Ch2 Avg [MPa] | Mesurements of average stresses in Strain Gauge 1 (SG on chanel 2) in last 30 seconds before recording
38 | Stress1 Ch2 MaxAvg [MPa] | Mesurements of Maximum stresses in Strain Gauge 1 (SG on chanel 2) in last 30 seconds before recording
39 | Stress1 Ch2 MinAvg [MPa] | Mesurements of minimum stresses in Strain Gauge 1 (SG on chanel 2) in last 30 seconds before recording
40 | Stress1 Ch2 StdDev [MPa] | Standard deviation of measured stresses by SG 1 (on chanel 2) in last 30 seconds before recoding
41 | Stress1 Ch2 Fcross [Hz] | It is allways zero
42 | Stress2 Ch1 Avg [MPa] | Mesurements of average stresses in Strain Gauge 2 (SG on chanel 1) in last 30 seconds before recording | It is leg No. 2!
43 | Stress2 Ch1 MaxAvg [MPa] | Mesurements of Maximum stresses in Strain Gauge 2 (SG on chanel 1) in last 30 seconds before recording
44 | Stress2 Ch1 MinAvg [MPa] | Mesurements of minimum stresses in Strain Gauge 2 (SG on chanel 1) in last 30 seconds before recording
45 | Stress2 Ch1 StdDev [MPa] | Standard deviation of measured stresses by SG 2 (on chanel 1) in last 30 seconds before recoding
46 | Stress2 Ch1 Fcross [Hz] | It is allways zero
47 | Stress2 Ch2 Avg [MPa] | Mesurements of average stresses in Strain Gauge 2 (SG on chanel 2) in last 30 seconds before recording
48 | Stress2 Ch2 MaxAvg [MPa] | Mesurements of Maximum stresses in Strain Gauge 2 (SG on chanel 2) in last 30 seconds before recording
49 | Stress2 Ch2 MinAvg [MPa] | Mesurements of minimum stresses in Strain Gauge 2 (SG on chanel 2) in last 30 seconds before recording
50 | Stress2 Ch2 StdDev [MPa] | Standard deviation of measured stresses by SG 2 (on chanel 2) in last 30 seconds before recoding
51 | Stress2 Ch2 Fcross [Hz] | It is allways zero
52 | Stress3 Ch1 Avg [MPa] | Mesurements of average stresses in Strain Gauge 3 (SG on chanel 1) in last 30 seconds before recording | It is leg No. 3!
53 | Stress3 Ch1 MaxAvg [MPa] | Mesurements of Maximum stresses in Strain Gauge 3 (SG on chanel 1) in last 30 seconds before recording
54 | Stress3 Ch1 MinAvg [MPa] | Mesurements of minimum stresses in Strain Gauge 3 (SG on chanel 1) in last 30 seconds before recording
55 | Stress3 Ch1 StdDev [MPa] | Standard deviation of measured stresses by SG 3 (on chanel 1) in last 30 seconds before recoding
56 | Stress3 Ch1 Fcross [Hz] | It is allways zero
57 | Stress3 Ch2 Avg [MPa] | Mesurements of average stresses in Strain Gauge 3 (SG on chanel 2) in last 30 seconds before recording
58 | Stress3 Ch2 MaxAvg [MPa] | Mesurements of Maximum stresses in Strain Gauge 3 (SG on chanel 2) in last 30 seconds before recording
59 | Stress3 Ch2 MinAvg [MPa] | Mesurements of minimum stresses in Strain Gauge 3 (SG on chanel 2) in last 30 seconds before recording
60 | Stress3 Ch2 StdDev [MPa] | Standard deviation of measured stresses by SG 3 (on chanel 2) in last 30 seconds before recoding
61 | Stress3 Ch2 Fcross [Hz] | It is allways zero
62 | Stress4 Ch1 Avg [MPa] | Mesurements of average stresses in Strain Gauge 4 (SG on chanel 1) in last 30 seconds before recording
63 | Stress4 Ch1 MaxAvg [MPa] | Mesurements of Maximum stresses in Strain Gauge 4 (SG on chanel 1) in last 30 seconds before recording
64 | Stress4 Ch1 MinAvg [MPa] | Mesurements of minimum stresses in Strain Gauge 4 (SG on chanel 1) in last 30 seconds before recording
65 | Stress4 Ch1 StdDev [MPa] | Standard deviation of measured stresses by SG 4 (on chanel 1) in last 30 seconds before recoding
66 | Stress4 Ch1 Fcross [Hz] | It is allways zero
67 | Stress4 Ch2 Avg [MPa] | Mesurements of average stresses in Strain Gauge 4 (SG on chanel 2) in last 30 seconds before recording
68 | Stress4 Ch2 MaxAvg [MPa] | Mesurements of Maximum stresses in Strain Gauge 4 (SG on chanel 2) in last 30 seconds before recording
69 | Stress4 Ch2 MinAvg [MPa] | Mesurements of minimum stresses in Strain Gauge 4 (SG on chanel 2) in last 30 seconds before recording
70 | Stress4 Ch2 StdDev [MPa] | Standard deviation of measured stresses by SG 4 (on chanel 2) in last 30 seconds before recoding
71 | Stress4 Ch2 Fcross [Hz] | It is allways zero